APPROVED PRODUCTION FACILITIES

Information Sheet

This information sheet is intended to assist building owners, managers and location managers in determining whether a building may be classified as an Approved Production Facility or is a Production Location.  This information sheet is based upon the requirements of California Fire Code, Article 46 - Motion Picture and Television Production Studio Sound Stages, Approved Production Facilities and Production Locations.

Definitions

Approved Production Facility is an existing building, or portion of a building, or a group of buildings altered for use by the entertainment industry for the purpose of motion picture, television and commercial production.

Production Location is any area or facility outside a production studio, approved production facility or sound stage used by the entertainment industry for the purpose of motion picture, television and commercial production.

Occupancy Classification

An ‘Approved Production Facility’ is classified as a Group F, Division 1 Occupancy.

Any building proposed for use as an “Approved Production Facility” must meet all requirements of the Uniform Building Code for such use.

If the use of an Approved Production Facility is changed, i.e., for live audience shows or wrap party, a permit is required from the Culver City Fire Department.  A Fire Safety Officer (FSO) may also be required.

General Requirements - Approved Production Facilities

- Perimeter aisles shall be provided.  Aisles shall have a minimum clear width of 4 feet and a minimum clear height of 7 feet.  The aisles shall be identified by 4-inch wide yellow stripes at the edges or other approved methods.

- The maximum travel distance to any exit shall be 150 feet.

- Exit doors shall be equipped with panic hardware and swing in the direction of travel.

- Illuminated exit signs shall be installed at all exits and where needed to guide occupants to an exit.

- Exit path illumination shall be provided by an approved emergency back-up system in the event of a power failure.

- Means of egress shall be maintained at all times.

- All foam plastics shall have a maximum heat-release rate of 100 kilowatts when tested in accordance with nationally recognized standards.

Fire Extinguishing Systems

- Approved Production Facilities shall be equipped with an approved automatic fire sprinkler system.  The system shall be designed to meet the requirements of NFPA 13, Extra Hazard, Group 2.

- All interior solid-ceiling sets over 600 square feet in area shall be protected by an automatic fire sprinkler system.

- All platforms over 600 square feet and which exceed three feet in height shall be protected by an automatic sprinkler system.

Solid-Ceiling Sets and Platforms - Fire Sprinkler Alternative

- Approved and listed heat detectors may be installed under interior solid-ceiling sets over 600 square fee in area and under platforms over 600 square feet and which exceed three feet in height.

- Heat detectors shall be spaced a maximum of 30 feet on center or in accordance with the manufacturer’s instructions.

- Heat detectors shall be connected to an approved and listed central

station service.

- Sets with solid-ceilings over 600-square feet shall be positioned to allow the operation of the automatic fire sprinkler system after production work has been completed for the day.

Fire Detection Equipment

- Fire alarm panels shall be State Fire Marshal listed and shall be utilized in accordance with their listing.

- Panels may be temporarily supported by sets, platforms or pedestals.

- Heat detectors required by this information shall be defined as a portable system as it is intended to be moved and reinstalled as necessary when sets or platforms are changed.

Design Requirements

- The Fire Department shall be provided with certification that the approved production facility will sustain the anticipated loads of sets, props, lighting or other temporary modifications.

- Where the anticipated loads exceed the design criteria the building or portions thereof shall be modified for the additional loads.

Electrical Requirements

- An Approved Production Facility shall be provided with a minimum of 35 watts per square foot of permanently installed power dedicated for the distribution of production lighting and power.  Mobile generators may be used for auxiliary power.

- All distribution equipment shall be designed for sound stage use.  The wiring to such equipment shall be permanent and shall comply with California Electrical Code.

- Temporary feeders shall not be tapped from panelboards and switchboards where deadfront covers have to be removed.

- Electrical panel “tap-in’s” are allowed at Production Locations which have 	been inspected by Building & Safety.

- Permanent or temporary equipment shall be installed in accordance with the California Electrical Code.  Such equipment shall not obstruct exits, means of egress or fire department access.  No power cables in the width of an exit door.

- Portable, mobile or stationary power-generating equipment may be used to supplement building electrical power for temporary wiring.  Equipment shall be located at a pre-designated location approved by the Fire Department.

- Temporary auxiliary power cables supplied from mobile generators or adjacent buildings may pass through exterior walls and interior fire-resistive walls provided an approved through-penetration fire-stop system is utilized for the protection of the opening.  Cables cannot pass through an exit door.

Mechanical Equipment

All auxiliary heating, ventilation and air-conditioning equipment shall be approved and listed for the intended use.  Flexible duct, if utilized, shall be noncombustible.  Such auxiliary equipment shall not obstruct exits, means of egress or fire department access.

Fire Permits

Fire Permits are required from the Culver City Fire Department, Fire Prevention Division at 9770 Culver Blvd., Culver City Ca. 90230 , Phone (310) 253-5925 for the following activities, operations, practices or functions:

- Candles and Open Flames such as prop fire places and cooking appliances.**

- Dust producing operations such as interior wood working.*

- Flammable or combustible liquids.*  (Class I Liquids in excess of 5 gallons and Class II and Class III Liquids in excess of 25 gallons).

- Live Audience in attendance during production.**

- Parking of vehicles inside a structure.***

- Pyrotechnical and Flame Special Effects.***

- Spraying with flammable or combustible liquids.*

- Tents (3 or more sides covered) in excess of 200 sq. ft. and canopies in excess of 400 sq. ft.***

- Welding or hot cutting operations.*

- Wrap parties.***

*	denotes Annual Fire Permit

** 	denotes Fire Permit for a specific type at a fixed location or a Fire Permit for each use or occurrence of different type or location.

***	denotes Fire Permit for each use or occurrence.

Fire Safety Officers

- Required for all productions where pyrotechnic special effects are used.

- Required for productions where flame special effects are used.

- Required at Production Locations.

- Required at Live Audience in attendance during production and wrap parties.

- Not required for candles, prop fire places or cooking appliances when a Fire Permit has been obtained from the Fire Prevention Bureau.

- Not required when all the provisions of this Information Sheet are met.